Liquefied Petroleum Gas Market Regulations – S.L. 545.20

Requalification for LPG Tank

Disclaimer

This ‘Report on LPG Tank Requalification’ is intended to be used only as a basic document to serve as a basis for the requalification by the competent person on LPG Tank as required by the Regulator for Energy and Water Services. The competent person and the plant manager/Authorised person shall undertake to add any necessary data and information together with this report if necessary.  This report does not exonerate the Competent Person from his professional obligations and duties.  Neither should it be construed as, and/or should in any way be understood and/or be deemed to exonerate the Competent Person and/or the Authorised person from being obliged to observe, comply with or carry out any requirement or comply with a provision of any law or any other legal requirement for the time being in force.  REWS makes no warranty about the content of this document and cannot be held liable under any circumstances for any direct or indirect damages resulting from its use.

- General

| REPORT REFERENCE No.: |  | SEC. STORAGE REWS AUTHORISATION No.: |  | REQUILIFICATION DATE: |  |
| --- | --- | --- | --- | --- | --- |
| AUTHORISED PERSON DETAILS |  |  | PLANT MANAGER DETAILS |  |  |
| Name: |  |  | Name: |  |  |
| ID Number: |  |  | ID Number: |  |  |
| Address: |  |  | Address: |  |  |
| Land Line No.: | Mobile No.: |  | Land Line No.: |  | Mobile No.: |

Installation Details – LPG Bulk Tank

| LPG Bulk Tank |  |  |
| --- | --- | --- |
| Address of authorised facility: |  | CATEGORY: Commercial Industrial Domestic |
| Tank Details | Tank |  |
| Tank Brand: |  |  |
| Tank Capacity (m³): |  |  |
| Tank Serial Number: |  |  |
| Tank Year of Manufacture: |  |  |
| Tank Installation Date: |  |  |
| Tank Location | Above Ground Buried / Mounded |  |

- Requalification Test Methods and Results for LPG Bulk  Vessels

  - Tests to be performed on LPG bulk vessels

| Type of LPG Bulk Tank | Tests to be performed |
| --- | --- |
| Above Ground (up to and including 13m3) | Tests 1, 2 and at least one of the following: 3, 4, 5, 6, 10. |
| Above Ground greater than 13m3 | Tests 1, 2, 11, 12, 13 and at least one of the following: 3, 4, 5, 6,10. |
| Below Ground (up to and including 13m3) | Test 1 and at least one from 3, 4, 5, 6, 10 and at least one from 2, 7, 8, 9. |
| Below Ground greater than 13m3 | Tests 1, 11, 12, 13 and at least one from 3, 4, 5, 6, 10 and at least one from 2, 8. |

  - Tests

| TEST METHODS |  |  | Test Result (Pass/ Fail/ NA) |
| --- | --- | --- | --- |
| 1 | Pressure Relief Valve | The Competent Person shall either: - Perform a test of the set pressure of the pressure relief valve and, for an external pressure relief valve, a check on the condition of the spring; or |  |
|  |  | - Replace the pressure relief valve with a new or reconditioned valve if required. |  |
| 2 | External Visual Inspection | External Visual Inspection as per EN12817. This test is required to detect surface defects on the tank shell and competent person must check for the following: - Deterioration of coating; - Corrosion; - Cracks, dents, gouges, lamination and bulges; - Inclinations and subsidence. Method of external visual inspection – refer to EN12817 |  |
| 3 | Internal Visual Inspection | The Competent Person shall check that the surfaces are free from corrosion and mechanical damage using an endoscope, camera or other means. |  |
| 4 | Hydraulic Pressure Test | Method of Hydraulic Pressure Test – refer to EN12817 |  |
| 5 | Acoustic Emission Test | Method of Acoustic Emission Testing – refer to EN12817. If this method is chosen, the Competent Person must present to the Regulator the test results issued by an NDT qualified technician. |  |
| 6 | Ultra Sonic Thickness test | Method of Thickness Checks – refer to EN12817. If this method is chosen, the Competent Person must present to the Regulator the test results issued by an NDT qualified technician. |  |
| 7 | External Monitoring by Camera for underground tanks | This type of inspection can only be applied to underground tanks that are enclosed in a protective envelope. Method of external monitoring – refer to EN12817. |  |
| 8 | Cathodic Protection Monitoring | Methods for Cathodic Protection monitoring – refer to EN12817. |  |
| 9 | Moisture Detection | This type of inspection can only be applied to underground tanks that are enclosed in a protective envelope that can be continuously monitored for water. Method for corrosion monitoring by moisture and condensation detection for underground tanks is found in EN12817I. |  |
| 10 | Any other method equivalent to any of the above | Competent Person is required to inform in detail any other equivalent method used for the recertification of the LPG tank. A method statement is to be submitted together with the test results. |  |
| 11 | Studs, bolts, nuts, and washers | Studs, bolts, nuts and washers shall be checked for damage or severe corrosion and replaced if necessary. |  |
| 12 | Emergency Valves | Excess flow valves and non-return valves shall be checked for correct operation. |  |
| 13 | Gaskets | Gaskets between any separated connections shall be renewed before reconnecting. |  |

- Certification by Competent Person

| Full Name: | ID Card No.: | REWS Competent person No.: |
| --- | --- | --- |
| Address: |  | Land Line Tel. No.: |
|  |  | Mobile No.: |
|  |  | E-mail Address: |
| I, the undersigned competent person, hereby declare that I have re-qualified the LPG storage tank described in Section 2.0 on __________________ (insert requalification date) and that this assessment report is a true and correct report of the inspection. I examined the LPG tank in accordance with the relevant Codes of Practice A2 and standards EN12817 and EN12819 where applicable. Thus I certify that the tank is fit for use / not fit for use. The next requalification by a competent person is to be done on __________________ (insert next requalification date). _________________________________ ___________________________ Signature of Competent Person & Date Official Rubber Stamp |  |  |

- Data Protection Notice

In processing your personal data, the Regulator will comply with binding legislative requirements imposed by the General Data Protection Regulation EU 2016/679 (the “GDPR”) and national Maltese law requiring an adequate data protection standard.

The processing of your personal data by the Regulator shall be done in the performance of a task carried out in the public interest or in the exercise of official authority vested in the Regulator and, or in compliance with a legal obligation.

In terms of these legal bases, the Regulator sometimes shares your personal information with third parties, including Government Departments (such as the Department of Customs, the Department of Health, the Civil Protection Department), other regulatory authorities (such as the Transport Authority, the Occupational Health and Safety Authority, the Planning Authority, the Environment and Resources Authority, the Malta Competition and Consumer Affairs Authority) and other Government Agencies and entities such as the Energy and Water Agency and the National Statistics Office.

You may access the Regulator’s Data Privacy Policy at: https://www.rews.org.mt/#/en/a/51-privacy-policy

If different from Section 1.0