Liquefied Petroleum Gas Market Regulations – S.L. 545.20

Periodic Inspection Report For LPG Secondary Storage Installations

Disclaimer

This ‘Periodic Inspection Report’ is intended to be used only as a basic document by the competent person on LPG Secondary Storage Facilities as required by the Regulator for Energy and Water Services. The competent person and the plant manager/Authorised person shall undertake to add any necessary data and information together with this report if necessary.  This report does not exonerate the Competent Person from his professional obligations and duties.  Neither should it be construed as, and/or should in any way be understood and/or be deemed to exonerate the Competent Person and/or the Authorised person from being obliged to observe, comply with or carry out any requirement or comply with a provision of any law or any other legal requirement for the time being in force.  REWS makes no warranty about the content of this document and cannot be held liable under any circumstances for any direct or indirect damages resulting from its use.

- General

| REPORT REFERENCE No.: |  | SEC. STORAGE REWS AUTHORISATION No.: |  | INSPECTION DATE: |  |
| --- | --- | --- | --- | --- | --- |
| AUTHORISED PERSON DETAILS |  |  | PLANT MANAGER DETAILS |  |  |
| Name: |  |  | Name: |  |  |
| ID Number: |  |  | ID Number: |  |  |
| Address: |  |  | Address: |  |  |
| Land Line No.: | Mobile No.: |  | Land Line No.: |  | Mobile No.: |

- Installation Details – LPG Bulk Tank

| LPG Bulk Tank |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Address of authorised facility: |  |  |  | CATEGORY: Commercial Industrial Domestic |  |  |  |
| Tank Details | Tank 1 |  | Tank 2 | Tank 3 | Tank 4 |  | Tank 5 |
| Tank Brand: |  |  |  |  |  |  |  |
| Tank Capacity (Litres): |  |  |  |  |  |  |  |
| Tank Serial Number |  |  |  |  |  |  |  |
| Tank Year of Manufacture |  |  |  |  |  |  |  |
| Tank Installation Date |  |  |  |  |  |  |  |
| Tank Location | Above Ground Buried / Mounded |  | Above Ground Buried / Mounded | Above Ground Buried / Mounded | Above Ground Buried / Mounded |  | Above Ground Buried / Mounded |
| Tank Condition | Reconditioned |  | Reconditioned | Reconditioned | Reconditioned |  | Reconditioned |
| LPG Interconnected cylinders (150kg or six or more interconnected portable LPG cylinders whichever the lower) |  |  |  |  |  |  |  |
| Address of authorised facility: |  |  |  | CATEGORY: Commercial Industrial Domestic |  |  |  |
| Total No. of connected cylinders: 0 |  | Total weight of connected cylinders (kg): 0 |  | Total No. of spare cylinders: 0 |  | Total weight of spare cylinders (kg): 0 |  |

- Periodic Inspection Checklist for LPG Bulk Tanks Installations

  - Inspection of Storage Site

| No. | INSPECTION CHECKS | FINDINGS | CORRECTIVE ACTION / RATIONALE | TARGET DATE | IMPLEMENTATION DATE |
| --- | --- | --- | --- | --- | --- |
|  | Check that the area around bulk vessels is free of flammable/combustible materials. |  |  |  |  |
|  | Check that the area immediately around the bulk vessel is clear of any vegetation. |  |  |  |  |
|  | Check that there have been no obvious changes to the bulk vessel installation or immediate surroundings and that there is no obvious ground movement. |  |  |  |  |
|  | Check that natural ventilation is still adequate. |  |  |  |  |
|  | Check that the condition of concrete pads and piers is satisfactory. |  |  |  |  |
|  | Check that there are no signs of differential settlement. |  |  |  |  |
|  | Anchoring bolts shall be visually inspected for deterioration, where fitted and accessible. |  |  |  |  |

  - Inspection of Tank

| No. | INSPECTION CHECKS | FINDINGS | CORRECTIVE ACTION / RATIONALE | TARGET DATE | IMPLEMENTATION DATE |
| --- | --- | --- | --- | --- | --- |
|  | Above- ground vessel(s) shall be checked for signs of corrosion, significant paintwork deterioration or other damage on the vessel; its supports; and any fire resisting coatings. Refer to Section 7 in Standard EN12817:2010 or EN12819:2009 where applicable. |  |  |  |  |
|  | Underground/Mounded vessel(s) shall be checked for signs of corrosion or damage. This is to be done to the visible parts of the vessel. |  |  |  |  |

  - Inspection of Tank fittings and Immediate pipework

| No. | INSPECTION CHECKS | FINDINGS | CORRECTIVE ACTION / RATIONALE | TARGET DATE | IMPLEMENTATION DATE |
| --- | --- | --- | --- | --- | --- |
|  | Tank fittings and immediate pipework shall be inspected for corrosion, damage or for obvious signs of leaks. |  |  |  |  |
|  | Check the status of any inoperative or leaking filler valves. Inspection of any worn or damaged filler valve thread or connection. |  |  |  |  |
|  | Valve hand wheels or levers shall be checked to ensure that they are free to move the valve stem. |  |  |  |  |
|  | Check that the pipework supports are secure and in a satisfactory condition. |  |  |  |  |
|  | Check that any studs, bolts, nuts and washers are free from any damage or severe corrosion and replace if required. |  |  |  |  |
|  | Perform any check required for the selected corrosion protection system, as detailed in the written scheme. |  |  |  |  |

  - Inspection of Pressure Relief Valve

| No. | INSPECTION CHECKS | FINDINGS | CORRECTIVE ACTION / RATIONALE | TARGET DATE | IMPLEMENTATION DATE |
| --- | --- | --- | --- | --- | --- |
| ##### 3.4.1 | Perform a test of the set pressure of the pressure relief valve and, for an external pressure relief valve, check the condition of the spring; or the pressure relief valve shall be replaced with a new or reconditioned valve if required. |  |  |  |  |
| ##### 3.4.2 | Check that the pressure relief valve drain hole is clear. |  |  |  |  |
| ##### 3.4.3 | Check that the stack pipes are free from corrosion. The pressure relief valve shall also be externally inspected if corrosion is found in the stack pipe. |  |  |  |  |
| ##### 3.4.4 | Check that rain caps are present and in good condition. |  |  |  |  |
| ##### 3.4.5 | For LPG vessels greater than 13m³, check that the multiport mechanisms can move freely into position when operated. |  |  |  |  |

  - Inspection of Pressure Gauge and Pressure Switch

| No. | INSPECTION CHECKS | FINDINGS | CORRECTIVE ACTION / RATIONALE | TARGET DATE | IMPLEMENTATION DATE |
| --- | --- | --- | --- | --- | --- |
|  | The pressure gauge, if fitted, shall be checked against a test gauge or replaced. |  |  |  |  |
|  | For LPG vessels greater than 13m³, if pressure switches are fitted check for correct operation by using a calibrated test pressure gauge. |  |  |  |  |

  - Inspection of Shut-Off Valves

| No. | INSPECTION CHECKS | FINDINGS | CORRECTIVE ACTION/RATIONAL | TARGET DATE | IMPLEMENTATION DATE |
| --- | --- | --- | --- | --- | --- |
|  | Test the shut-off valve for correct functionality. Check for corrosion and damage. Replace if required (refer to Section 5.2 of COPA2). |  |  |  |  |
|  | Blanked or plugged liquid phase valves shall be checked for external leakage. |  |  |  |  |

  - Inspection of Excess Flow Valves, Non-Return Valves & Remotely operated Valves

| No. | INSPECTION CHECKS | FINDINGS | CORRECTIVE ACTION/RATIONAL | TARGET DATE | lMPLEMENTATION DATE |
| --- | --- | --- | --- | --- | --- |
|  | Check that excess flow valves and non-return valves are operating in accordance with manufacturer’s recommendations or a written procedure. Replace if required. |  |  |  |  |
|  | For LPG systems greater than 13m³, check that the remotely operated valves (if fitted) operate correctly when fitted. |  |  |  |  |

  - Inspection of Temperature Gauges (where fitted)

| No. | INSPECTION CHECKS | FINDINGS | CORRECTIVE ACTION/RATIONAL | TARGET DATE | IMPLEMENTATION DATE |
| --- | --- | --- | --- | --- | --- |
|  | Check that gauges are checked for operation in accordance with manufacturer’s recommendations or a written procedure. Replace if necessary |  |  |  |  |

  - Inspection of Pull-Away/Breakaway Couplings

| No. | INSPECTION CHECKS | FINDINGS | CORRECTIVE ACTION/RATIONAL | TARGET DATE | IMPLEMENTATION DATE |
| --- | --- | --- | --- | --- | --- |
|  | Check that couplings are operating as per manufacturer’s recommendations or a written procedure. Replace if required. |  |  |  |  |

  - Inspection of Contents Gauge

| No. | INSPECTION CHECKS | FINDINGS | CORRECTIVE ACTION/RATIONAL | TARGET DATE | IMPLEMENTATION DATE |
| --- | --- | --- | --- | --- | --- |
|  | Check that gauges are operating in accordance to the manufacturer’s recommendations or a written procedure. Replace if required. |  |  |  |  |
|  | The contents gauging overfill protection and/or stop-fill devices shall be checked for effectiveness. The gauging devices or contents gauges that bleed to the atmosphere (e.g. rotary tubes, fixed tubes or slip tubes) shall be tested when filling the tank. Other types of contents gauges shall be checked as required (e.g. during product transfer to or from the tank). |  |  |  |  |

  - Inspection of Fixed Liquid Level Gauge

| No. | INSPECTION CHECKS | FINDINGS | CORRECTIVE ACTION/RATIONAL | TARGET DATE | IMPLEMENTATION DATE |
| --- | --- | --- | --- | --- | --- |
|  | Check that the fixed liquid level gauge is operating as per manufacturer’s recommendations or a written procedure. Replace if required. |  |  |  |  |

  - Inspection of Regulators and Associated Safety Devices

| No. | INSPECTION CHECKS | FINDINGS | CORRECTIVE ACTION/RATIONAL | TARGET DATE | IMPLEMENTATION DATE |
| --- | --- | --- | --- | --- | --- |
|  | Check the condition of regulators and any associated safety devices in accordance with a written procedure. Replace if required. |  |  |  |  |

  - Inspection of Valve Cover

| No. | INSPECTION CHECKS | FINDINGS | CORRECTIVE ACTION/RATIONAL | TARGET DATE | IMPLEMENTATION DATE |
| --- | --- | --- | --- | --- | --- |
|  | Check that the valve cover, if fitted, is in place, undamaged and able to be locked. |  |  |  |  |

  - Inspection of Bonding (where applicable)

| No. | INSPECTION CHECKS | FINDINGS | CORRECTIVE ACTION/RATIONAL | TARGET DATE | IMPLEMENTATION DATE |
| --- | --- | --- | --- | --- | --- |
|  | Check that an earthing rod is in position and securely connected to the vessel. |  |  |  |  |
|  | Check that there is an earthing point or bonding connection for use by the bulk delivery tanker. |  |  |  |  |

  - Inspection of Electrical Equipment

| No. | INSPECTION CHECKS | FINDINGS | CORRECTIVE ACTION/RATIONAL | TARGET DATE | IMPLEMENTATION DATE |
| --- | --- | --- | --- | --- | --- |
|  | Check that all ancillary electrical equipment including cables and connections, particularly flameproof connections, switches etc. are in satisfactory condition in accordance with manufacturer’s/installer’s instructions or other schedules prepared by a person competent in electrical matters. |  |  |  |  |

  - Inspection of the Storage Compound Protection (where applicable)

| No. | INSPECTION CHECKS | FINDINGS | CORRECTIVE ACTION/RATIONAL | TARGET DATE | IMPLEMENTATION DATE |
| --- | --- | --- | --- | --- | --- |
|  | Check that fencing is in good condition. |  |  |  |  |
|  | Check that there are at least two outward opening gates and that these are free to open correctly. |  |  |  |  |
|  | Check that any protective kerbs, barriers etc. are in good condition |  |  |  |  |

  - Inspection of the Warning Notices and Fire Precautions

| No. | INSPECTION CHECKS | FINDINGS | CORRECTIVE ACTION/RATIONAL | TARGET DATE | IMPLEMENTATION DATE |
| --- | --- | --- | --- | --- | --- |
|  | Check that statutory notices on the vessel and compound (where applicable) are up to date and readable from the separation distances given in the COP A1. |  |  |  |  |
|  | Check that fire extinguishers are being tested and maintained at regular intervals as per COPA2 Section 5.8. |  |  |  |  |
|  | Check that firewater hoses, nozzles, fire pump water spray systems and initiating systems do operate according to the supplier’s instructions or other schedules prepared by a person competent in fire protection system. |  |  |  |  |
|  | Check that Alarm system is tested regularly. |  |  |  |  |

  - Periodic Inspection Checklist for LPG Cylinder Storage Installations

| No. | INSPECTION CHECKS | FINDINGS | CORRECTIVE ACTION / RATIONALE | TARGET DATE | IMPLEMENTATION DATE |
| --- | --- | --- | --- | --- | --- |
| 4.1 | Cylinder installation without a suitable stable base. |  |  |  |  |
| 4.2 | Cylinder installation sited too close to fixed ignition source. |  |  |  |  |
| 4.3 | Battery of cylinders connected to an automatic change over device without OPSO protection. |  |  |  |  |
| 4.4 | Cylinder installation regulators fitted at a height below that of the cylinder outlet valve. |  |  |  |  |

  - Additional observations by Competent Person

| No. | INSPECTION CHECKS | FINDINGS | CORRECTIVE ACTION | TARGET DATE | IMPLEMENTATION DATE |
| --- | --- | --- | --- | --- | --- |

- Replacement of Parts

| Item replaced | Remarks |
| --- | --- |
| Pressure Relief Valve |  |
| Contents Gauge |  |
| Fill Valve |  |
| Vapour take-off Valve |  |

- Additional Tests / Examinations Carried out by the Competent Person

| Test | Remarks |
| --- | --- |

- Additional Remarks by Competent Person (if any)

9.0   Certification by Competent Person

| Full Name: | ID Card No.: | REWS Competent person No.: |
| --- | --- | --- |
| Address: |  | Land Line Tel. No.: |
|  |  | Mobile No.: |
|  |  | E-mail Address: |
| I, the undersigned competent person, hereby declare that I have inspected the LPG secondary storage facility described in Section 2.0 on __________________ (insert inspection date) and that this assessment report is a true and correct report of the inspection. I certify this installation safe for use and it shall be due for the next inspection by a competent person on __________________ (insert next Inspection date). _________________________________ Signature of Competent Person & Date Official Rubber Stamp |  |  |

11.0    Declaration by Authorised person

I, the undersigned Authorised person of the above-certified Facility described in Section 2.0, declare that I have understood all the contents of this report, after such contents were explained to me by the competent person. I agree to implement the corrective actions as described in this report by not later than the target dates specified.   Furthermore I declare that I will submit another follow-up Inspection report to the Regulator for Energy and Water Services as per above specified due date.  I also understand that in the case of failure to implement the agreed corrective actions and to submit the necessary proof of their implementation thereof, I shall be making myself liable for any necessary action by the Regulator for Energy and Water Services. I understand and agree that the Regulator may require further inspections to be made when so required.

________________________________________

Signature of Authorised person & Date

12.0   Data Protection Notice

In processing your personal data, the Regulator will comply with binding legislative requirements imposed by the General Data Protection Regulation EU 2016/679 (the “GDPR”) and national Maltese law requiring an adequate data protection standard.

The processing of your personal data by the Regulator shall be done in the performance of a task carried out in the public interest or in the exercise of official authority vested in the Regulator and, or in compliance with a legal obligation.

In terms of these legal bases, the Regulator sometimes shares your personal information with third parties, including Government Departments (such as the Department of Customs, the Department of Health, the Civil Protection Department), other regulatory authorities (such as the Transport Authority, the Occupational Health and Safety Authority, the Planning Authority, the Environment and Resources Authority, the Malta Competition and Consumer Affairs Authority) and other Government Agencies and entities such as the Energy and Water Agency and the National Statistics Office.

You may access the Regulator’s Data Privacy Policy at: https://www.rews.org.mt/#/en/a/51-privacy-policy

Where Corrective Actions are still pending, the next inspection date should not be later than the latest target date.  In the case of no pending Corrective Actions, next inspection date should not be in excess of twenty-four months from the date of this inspection report.